## Application Matrix
|  | Relative Level of Effort Scoring for Each Protocol Step (0 - 5 per step) | [5 empty] | Overall Level of Effort - Weighted [%]
Application |  | Project Definition | Data collection & Reconciliation | Model Set-Up | Calibration & Validation | Simulation & Results Interpretation | Total effort spent (max25) | Project Definition | Data collection & Reconciliation | Model Set-Up | Calibration & Validation | Simulation & Results Interpretation | Total effort spent (Weighted)
Weightings |  | 10 | 40 | 10 | 15 | 25 | 100
DESIGN
1 | Calculate Sludge Production | 1 | 3 | 2 | 3 | 1 | 10 | 2 | 24 | 4 | 9 | 5 | 44
| Notes | 1. Usually clear 2. Simple objective that can be defined easily. 3. Need to assess average and peak values. 4. Care taken if future production is objective. | 1. Pay particular attention to information for ISS and Xi (see section in Wastewater Characterisation) 2. Longer term average data should be used 3. Data on sludge streams often of poor quality and should be assessed carefully (see section on Data Reconci | 1. Simple model structure is usually sufficient for this objective 2. Mixed liquor wastage can be used if objective is just mass load produced. This makes the model easier to adjust MLSS. 3. All biokinetic models suitable for modelling and no customizati | 1. If sludge production and VSS don't match plant data then influent characteristics should be re-evaluated and may need adjustment | 1. Straightforward and simple interpretation. 2. Care should be taken when converting mass load produced to actual flows and solids concentrations
2 | Design Aeration System | 2 | 3 | 3 | 2 | 3 | 13 | 4 | 24 | 6 | 6 | 15 | 55
| Notes | Usually clear |  |  |  | Needs some comparison
3 | Develop a Process Configuration for Nitrogen Removal | 3 | 4 | 3 | 4 | 4 | 18 | 6 | 32 | 6 | 12 | 20 | 76
| Notes |  | Needs information on N spieces
4 | Develop a Process Configuration for Phosphorus Removal | 4 | 4 | 3 | 4 | 4 | 19 | 8 | 32 | 6 | 12 | 20 | 78
| Notes | We need to confirm the boundary for analysis
5 | Assess Plant Capacity for Nitrogen Removal | 4 | 5 | 3 | 5 | 4 | 21 | 8 | 40 | 6 | 15 | 20 | 89
Notes
6 | Design a Treatment System to Meet Peak Effluent Nitrogen Limits | 5 | 5 | 5 | 5 | 5 | 25 | 10 | 40 | 10 | 15 | 25 | 100
| Notes | We need to be careful on assumptions of scenario. |  |  | Needs dynamic calibration
OPERATION
7 | Optimise Aeration Control | 3 | 4 | 4 | 4 | 4 | 19 | 6 | 32 | 8 | 12 | 20 | 78
| Notes |  | We need dynamic data, but less details of data, makes average. | If the control strategies are convetional ones, it is relatively easy with existing simulators.
8 | Test Effect of Taking Tanks Out of Service | 2 | 3 | 3 | 3 | 3 | 14 | 4 | 24 | 6 | 9 | 15 | 58
| Notes |  |  | Average set up will be required.
9 | Use Model to Develop Sludge Wastage Strategy | 3 | 3 | 3 | 3 | 3 | 15 | 6 | 24 | 6 | 9 | 15 | 60
| Notes |  |  | Need models for side stream processes. | Same as sludge related design. | Comparison projects always need some extra effort.
10 | Develop a Strategy to Handle Storm Flows | 5 | 4 | 4 | 4 | 4 | 21 | 10 | 32 | 8 | 12 | 20 | 82
| Notes |  |  | We need extra effort to set up control strategies. |  | Comparison projects always need some extra effort.
TRAINING
11 | Develop a General Model for Process Understanding | 2 | 1 | 1 | 0 | 2 | 6 | 4 | 8 | 2 | 0 | 10 | 24
| Notes | What to teach requires repetitive discussion with the cliants | I assumed hypothetical plant. | I intend for some customized user interfaces for trainers |  | If we intend to prepare preinstalled interpretation we need great effort
12 | Develop a Site Specific Model for Operator Training | 3 | 4 | 4 | 4 | 4 | 19 | 6 | 32 | 8 | 12 | 20 | 78
| Notes | We need to confirm how the system will be used. | Need usual data for calibration, but may not be so intensive | I intend for some customized user interfaces for operators | Average effort for calibration | If we let operators interprit
INDUSTRIAL
13 | Develop Nitrogen Removal for Food Production Waste | 3 | 4 | 3 | 4 | 4 | 18 | 6 | 32 | 6 | 12 | 20 | 76
14 | Assess Acceptability of New Influent at a Petrochemical Site | 4 | 5 | 4 | 4 | 3 | 20 | 8 | 40 | 8 | 12 | 15 | 83
| Calculate Sludge Production | 1 | 3 | 2 | 3 | 1 | 10 | 2 | 24 | 4 | 9 | 5 | 44
| Design Aeration System | 2 | 3 | 3 | 2 | 3 | 13 | 4 | 24 | 6 | 6 | 15 | 55
| Develop a Process Configuration for Nitrogen Removal | 3 | 4 | 3 | 4 | 4 | 18 | 6 | 32 | 6 | 12 | 20 | 76
| Develop a Process Configuration for Phosphorus Removal | 4 | 4 | 3 | 4 | 4 | 19 | 8 | 32 | 6 | 12 | 20 | 78
| Assess Plant Capacity for Nitrogen Removal | 4 | 5 | 3 | 5 | 4 | 21 | 8 | 40 | 6 | 15 | 20 | 89
| Design a Treatment System to Meet Peak Effluent Nitrogen Limits | 5 | 5 | 5 | 5 | 5 | 25 | 10 | 40 | 10 | 15 | 25 | 100
| Optimise Aeration Control | 3 | 4 | 4 | 4 | 4 | 19 | 6 | 32 | 8 | 12 | 20 | 78
| Test Effect of Taking Tanks Out of Service | 2 | 3 | 3 | 3 | 3 | 14 | 4 | 24 | 6 | 9 | 15 | 58
| Use Model to Develop Sludge Wastage Strategy | 3 | 3 | 3 | 3 | 3 | 15 | 6 | 24 | 6 | 9 | 15 | 60
| Develop a Strategy to Handle Storm Flows | 5 | 4 | 4 | 4 | 4 | 21 | 10 | 32 | 8 | 12 | 20 | 82
| Develop a General Model for Process Understanding | 2 | 1 | 1 | 0 | 2 | 6 | 4 | 8 | 2 | 0 | 10 | 24
| Develop a Site Specific Model for Operator Training | 3 | 4 | 4 | 4 | 4 | 19 | 6 | 32 | 8 | 12 | 20 | 78
| Develop Nitrogen Removal for Food Production Waste | 3 | 4 | 3 | 4 | 4 | 18 | 6 | 32 | 6 | 12 | 20 | 76
| Assess Acceptability of New Influent at a Petrochemical Site | 4 | 5 | 4 | 4 | 3 | 20 | 8 | 40 | 8 | 12 | 15 | 83

## Objective Descriptions
IWA Good Modelling Practice
Application Matrix
Description of Objectives
12 typical modelling objectives were selected for the Matrix. The selected objectives are intended to cover the most common purposes for modelling, however it is not an exhaustive list. For objectives not included here, the user should select an objective that is similar and adjust the scoring accordingly.
The modelling objectives are grouped under 3 headings: Design, Operation and Training. A brief description of each of the objectives is given below.
DESIGN
1 | Calculate Sludge Production
In this application a model is constructed with the simple objective of estimating the quantity of sludge produced. Information from the model will be used in sizing equipment to handle the sludge. For this purpose average and peak quantities will need to be determined using the model.
2 | Design Aeration System
This model is used to design the aeration system of the activated sludge process. The model is used to determine the average and peak airflows to size blowers. The model is also used to determine the distribution of air (i.e. the taper) needed through the aeration basins to select the correct number and layout for diffusers.
3 | Develop a Process Configuration for Nitrogen Removal
In this application a number of models are constructed to determine which configuration gives the best nitrogen removal under different design load conditions. It is assumed that the models are developed for an existing plant that is either being upgraded to provide nitrogen removal or to improve existing nitrogen removal. Nitrogen removal is assessed based on monthly or annual average values.
4 | Develop a Process Configuration for Phosphorus Removal
In this application a number of models are constructed to determine which configuration gives the best phosphorus removal under different design load conditions. It is assumed that the models are developed for an existing plant that is being upgraded to provide biological phosphorus removal. Phosphorus removal is assessed based on monthly or annual average values.
5 | Assess Plant Capacity for Nitrogen Removal
In this application a model of an existing nitrogen removal plant is constructed. The model is used to determine the capacity of the plant to remove nitrogen under future - increasing load - conditions and/or tightening effluent nitrogen requirements. Capacity is assessed based on monthly or annual average values. The capacity is usually expressed as the maximum flow that can be treated by the plant to meet future flow and effluent requirements.
6 | Design a Treatment System to Meet Peak Effluent Nitrogen Limits
In this application a number of models are constructed to determine which configuration gives the best nitrogen removal under different design load conditions. It is assumed that the models are developed for an existing plant that is either being upgraded to provide nitrogen removal or to improve existing nitrogen removal. Nitrogen removal is assessed based on instantaneous values and so greater confidence is required in model predictions than for a plant with a monthly or annual average limit.
OPERATION
7 | Optimise Aeration Control
A model is developed for an existing activated sludge plant with basic DO control. The model is used to adjust or modify the aeration control system to achieve one or more of the following goals: reduce energy costs; reduce greenhouse gas emissions (including N2O); maximise treatment capcity; maximise effluent quality.
8 | Test Effect of Taking Tanks Out of Service
In this application a model is developed for an existing plant to be used to test the effect of major process changes such as taking tanks out of service for maintenance or construction activities. The model is used to test if the change will cause the plant to fail its effluent requirements for ammonia, total nitrogen or total phosphorus (on a monthly or annual average basis).
9 | Use Model to Develop Sludge Wastage Strategy
A model is developed for an existing activated sludge plant to investigate different sludge wastage strategies. Different wastage frequencies, quantities and control strategies are tested. The investigation will look at the stability of the activated sludge treatment system, the quantities and scheduling of sludge produced and the potential impact on sludge treatment processes.
10 | Develop A Strategy to Handle Storm Flows
A model of an existing plant is constructed and it is subjected to storm flow conditions. Different control strategies are tested on the model to determine which provides the plant with the best ability to cope with storm conditions. The focus of the investigations is on the ability of the control strategy to provide process robustness to mitigate the effects of storm conditions (e.g. peak effluent concentrations are reduced) and the speed with which the plant recovers from the effects of the storm.
TRAINING
11 | Develop a General Model for Process Understanding
A model of an activated sludge plant is constructed for the purpose of training operators, engineers and/or other personnel to help increase their process understanding. The model may be based on an exisiting plant or it may be purely hypothetical. The model will be used for a 1-hour training session and the level of effort considered includes time to produce presentation materials.
12 | Develop a Site Specific Model for Operator Training
A model of an existing activated sludge plant is constructed. The model is used to train operators, engineers and/or other personnel on the impact of making process changes to their plant. The model and presentation material are used to provide a total of 8 hours of training including some interactive "hands-on" work and model demonstration runs.
INDUSTIAL EXAMPLES
13 | Develop a Process Configuration for Nitrogen Removal Treating Waste from a Food Production Factory (Soy Sauce)
An existing factory consists of the full process of soy source production including soy bean processing, brewing and bottling. Current volumetric loading for the liquid waste is 500 m3/d and expected to be increased up to 700 m3/d within 5 years, influent BOD is about 1200 mg/L and TKN is not known. The existing treatment plant aeration tank total volume is 1000 m3, which consists of 3 tanks in series. A post coagulation process is installed for phosphorus removal. Rising sludge is occasionally observed in the secondary settler. In this application a number (up to three) models are constructed to determine which configuration gives the best nitrogen removal under current and future design load conditions. It is assumed the models are developed for an existing plant that currently provides full nitrification, but no denitrification and is being upgraded to improve existing nitrogen removal. Based on a preliminary site audit, intermittent aeration is proposed as one option. Nitrogen removal is assessed based on daily grab sample values with a target effluent limit of 10 mg/L for the sum of nitrate and nitrite nitrogen. This assessment needs to be carried out using dynamic models.
14 | Assess Acceptability of New Influent at a Petrochemical Site
A petrochemical complex has a wastewater plant with a reactor volume of 10,000 m3. The average influent load is 10,000 m3/d with an average COD of 1000 mg/L. The wastewater collection system is composed of three major streams. A new plant installation is scheduled within 2 years which will increase the influent by 2,000 m3/d. An effluent sample can be obtained from a pilot plant of the new facility. In this application, a model for the exiting plant is constructed to evaluate the acceptability of the new influent. Treated effluent COD, sludge production, aeration capacity and inhibitory effects are the main concern. This assessment can be evaluated using steady-state models.

## Scoring Notes
IWA Good Modelling Practice
Application Matrix
Introduction
This application matrix provides examples of typical modelling objectives and gives some guidance on the level of effort required to carry them out.
12 common objectives are listed in the matrix. The approach taken in developing this matrix can be applied to other similar objectives not explicitly listed.
Scoring
For each objective the relative level of effort is scored using a scale of 0 to 5 for each of the model development steps of the unified protocol.
The score is an indication of the relative level of effort required to carry out a particular step, with 5 meanining "maximum effort" and 0 meaning no effort for that particular step.
As a general guide, the following scoring system can be used:
| Score | Notes
No effort | 0 | Step does not have to be carried out and can be skipped
Minimal effort | 1 | Step needs to be considered but does not require great effort. Can potentially be carried out by an individual with little or no consultation.
Below average effort | 2 | Requires some effort and 1 or 2 key points described in the protocol may require more astutue attention.
Average effort | 3 | Medium level of effort for this step. Several points described in the protocol will have to be carried out.
Siginificant effort | 4 | More effort than average with almost all of the details of the protocol relevant, minus 1 or 2.
Maximum effort | 5 | This is a critical step and all of the details for it described in the protocol should be considered. Will require considerable consultation and collaboration with all involved.
For the Data Collection and Calibration/Validation steps the "Tiered Approach" suggested in Chapter 21 of the WERF Guidelines may be used:
WERF Designation | Suggested Score for Application Matrix |  | Notes
Level 1: Defaults & Assumptions Only | 0 - 1 |  | Generally only applicable to greenfield sites or applications where no data is available
Level 2: Historical Data Only | 2 - 3 |  | Use is made of available historical data - no extra sampling is done
Level 3: On-site, Full-scale Testing | 3 - 4 |  | Additional sampling and testing is carried out to supplement historical data
Level 4: Direct Parameter Measurements | 5 |  | Specialised bench-scale testing is carried out to determine rates
The WERF Guidelines link data collection with calibration effort. If a better calibration is needed then more and better data is needed.
This means that the effort required for data collection is driven by the effort required in calibration.
Also, the converse can be true. If more data is available then more effort is required to carry out the calibration.
Weightings
The different steps necessarily require different levels of effort (e.g. data validation requires considerably more time and effort than the other steps)
therefore weightings are applied to each of the raw scores to give an overall weighted "level of effort"
The weightings are as follows:
Weighting
Project Definition | 10
Data collection & reconcilliation | 40
Model Set-Up | 10
Calibration/ Validation | 15
Simulation & Results Interpretation | 25
The term "level of effort" is an indication of the relative amount of time required to carry out the modelling project.
It is also an indication of the cost required to carry it out.

## Benefits
# | Objectives | Benefits of Good Process Model Developed Using GMP | Averted Risks (Dangers if GMP Not Used)
DESIGN
1 | Calculate Sludge Production | Accurate prediction of sludge production. Equipment for handling sludge treatment correctly sized | Sludge handling equipment oversized (excessive cost), or undersized (operational problems)
2 | Design Aeration System | Aeration system correctly sized to account for system dynamics | Aeration system oversized - wasting energy, or undersized and unable to meet peak demands.
3 | Develop a Process Configuration for Nitrogen Removal | Robust design for Nitrogen Removal | Sub-optimal design
4 | Develop a Process Configuration for Phosphorus Removal | Robust design for Phosphorus Removal. Good understanding of process sensitivity to external factors. | Unstable ot inadequate design
5 | Assess Plant Capacity for Nitrogen Removal | Good assessment of plant capacity | Optimistic or pessimistic opinion of treatment capacity leading to bad decsions
6 | Design a Treatment System to Meet Peak Effluent Nitrogen Limits | Robust design. Good quantification of risk of not meeting permit and frequency of such events | Low confidence in design
OPERATION
7 | Optimise Aeration Control | Good suggestions for control optimisation | Inadequate control idea development
8 | Test Effect of Taking Tanks Out of Service | Confidence in taking tanks out of service | Potential for wrong decision to take tanks out of service and potential permit violation
9 | Use Model to Develop Sludge Wastage Strategy | Good idea development for sludge strategies | Inadequate assessment of strategies
10 | Develop a Strategy to Handle Wet Weather Flows | Robust strategy for wet weather events | Inadequate wet weather strategy
TRAINING
11 | Develop a General Model for Process Understanding | Clear and understandable training tool | Ambiguous and confusing example
12 | Develop a Site Specific Model for Operator Training | Useful tool to investigate process dynamics and plant response | Confusion or poor appreciation of plant dynamics
INDUSTRIAL
13 | Develop a Process Configuration for Nitrogen Removal Treating Waste from a Food Production Factory (Soy Sauce) | Robust design for industrial treatment | Inadequate plant design
14 | Assess Acceptability of New Influent at a Petrochemical Site | Confidence in treatment capabilities of new treatment facility | Inadequate plant design

## Data Needs
# | Objectives | Input Data of Primary Importance | Physical Data | Operational Settings | Performance Data | Additional Information | Required Frequency & Quantity of Input and Performance Data
DESIGN
1 | Calculate Sludge Production | CODtot,INF | Location of sludge wastage (e.g. RAS or ML) | Wastage Regime (Frequency, duration) | TSSML, TSSRAS, Fwas |  | Monthly average for past 3+ years
|  | TSSINF, VSSINF |  | Control approach for solids inventory (MLSS setpoint, SRT control etc)
2 | Design Aeration System | All flows and loads | Number and type of diffusers | DO set points, control scheme | Qair, Energy Use, So | Measurement or estimate of a-factor and fouling effects needed | Hourly Data for Diurnal Patterns & Peak Events
|  |  |  | Plant MLSS and SRT |  | Header pressure and blower system performance curves | Monthly Average Data for past 3+ years for Longer-term Loads & Seasonal Effects
3 | Develop a Process Configuration for Nitrogen Removal | CODtot,INF, TNINF | Anoxic Zone Size and Configuration | Recycle Flows, Additional Carbon (if any) | TNEFF |  | Monthly average for past 3+ years
Influent Fractions for COD and TN
4 | Develop a Process Configuration for Phosphorus Removal | CODtot,INF, TPINF, TNINF | Anaerobic and Anoxic zone Sizes and Configurations | Recycle Flows, Additional Carbon (if any) | TPEFF |  | Monthly average for past 3+ years
Influent Fractions for COD, TP and TN
5 | Assess Plant Capacity for Nitrogen Removal | CODtot,INF, TNINF |  |  |  |  | Monthly average for past 3+ years
|  | Influent Fractions for COD and TN |  |  |  |  | Hourly Data for Diurnal Patterns & Peak Events
6 | Design a Treatment System to Meet Peak Effluent Nitrogen Limits | CODtot,INF, TNINF | Anoxic Zone Size and Configuration | Recycle Flows, Additional Carbon (if any) | TNEFF |  | Hourly Data for Diurnal Patterns & Peak Events
|  | Influent Fractions for COD and TN |  |  |  |  | Monthly Average Data for past 3+ years for Longer-term Loads & Seasonal Effects
OPERATION
7 | Optimise Aeration Control | All flows and loads | Number and type of diffusers | DO set points, control scheme | Qair, Energy Use, So | Measurement or estimate of a-factor and fouling effects needed | Data every 5-minutes for 24 hr period
|  |  |  | Plant MLSS and SRT |  | Header pressure and blower system performance curves
8 | Test Effect of Taking Tanks Out of Service |  | Number and Configuration of Tanks | Log of number of tanks in service | Effluent Concentrations in Discharge Licence
9 | Use Model to Develop Sludge Wastage Strategy | CODtot,INF | Location of sludge wastage (e.g. RAS or ML) | Wastage Regime (Frequency, duration) | TSSML, TSSRAS, Fwas
|  | TSSINF, VSSINF |  | Control approach for solids inventory (MLSS setpoint, SRT control etc)
10 | Develop a Strategy to Handle Storm Flows | Dynamic Profile of Influent Flows and Loads During Storm Event |  |  | Effluent Concentrations in Discharge Licence
TRAINING
11 | Develop a General Model for Process Understanding
12 | Develop a Site Specific Model for Operator Training | CODtot,INF, TPINF, TNINF | Anaerobic and Anoxic zone Sizes and Configurations | Recycle Flows, Additional Carbon (if any) | TPEFF
Influent Fractions for COD, TP and TN
INDUSTRIAL
13 | Develop a Process Configuration for Nitrogen Removal Treating Waste from a Food Production Factory (Soy Sauce) | CODtot,INF, TNINF | Anoxic Zone Size and Configuration | Recycle Flows, Additional Carbon (if any) | TNEFF
Influent Fractions for COD and TN
14 | Assess Acceptability of New Influent at a Petrochemical Site | Respirometric Data

## Ch 6 table
|  | Simulation Type | [6 empty] | Inputs & Outputs
|  | Steady State Simulations |  | Dynamic Simulations | [6 empty] | Suggested Format
# | Objectives | Type | Purpose | Resolution | Type | Purpose | Notes | Sensitivity Analyses | Parameters/Manipulated Variables | Main Outputs | Summary Table | Time Series Graph | Bar Chart | Cumulative Distribution
DESIGN
1 | Calculate Sludge Production | Annual | Economic Analysis | [5 empty] | QWAS | FWAS kg d | x
|  | Monthly | Equipment Sizing | [7 empty] | x
2 | Design Aeration System | Annual | Economics, blower and diffuser type | Hourly | Typical Day | Define normal operating range for blower | Alternatively a Birthday Cake Analysis or a full year of hourly data simulation can be run to fulfill all 3 purposes |  |  | Qair, % coverage, airflow per diffuser | x | x |  | x
|  |  |  | Hourly | Maximum Day | Define peak air demand | [5 empty] | x |  | x
|  |  |  | Hourly | Minimum Day | Define minimum air demand | [5 empty] | x |  | x
3 | Develop a Process Configuration for Nitrogen Removal | Monthly Seasonal | Performance |  |  |  |  | COD:N | V, Qrec, conf | TN | x |  | x
4 | Develop a Process Configuration for Phosphorus Removal | Monthly Seasonal | Performance |  |  |  |  | COD:P, rbCOD and vfa fractions | V, Qrec, conf | TN TP | x |  | x
5 | Assess Plant Capacity for Nitrogen Removal | Monthly Seasonal | Capacity |  |  |  |  | COD:N, SRT vs Temperature | Q, qAir | TN | x |  | x
6 | Design a Treatment System to Meet Peak Effluent Nitrogen Limits | Monthly Seasonal | Short-list options | Hourly | Seasonal Weeks | Peak Effluent Nitrogen |  | COD:N | Qair, V, config | NH3 NO3 |  | x |  | x
OPERATION
7 | Optimise Aeration Control |  |  | Minutes | Week | Impact of control options |  |  | Qair, DO_setpoints | kWh, Qair, NH3, NO3, NO2, DO |  | x | x
8 | Test Effect of Taking Tanks Out of Service |  |  | Hourly | Week | Impact of operational change |  |  | number of tanks | NH3, Ntot, Ptot |  | x
9 | Use Model to Develop Sludge Wastage Strategy |  |  | Hourly | Month | Impact of operational changes |  |  | FWAS kg/d | MLSS |  | x
10 | Develop a Strategy to Handle Storm Flows | Annual or Monthly | Establish initial condtions | Hourly | Week | Repsonse to storm flows |  |  | Q, Eq Basin V | NH3, Ntot, Ptot, TSS |  | x
TRAINING
11 | Develop a General Model for Process Understanding |  |  | Hourly | Day or Week | Sludge Production |  |  | Typical control variables | Typical process indicators | x | x | x
|  |  |  | Minutes | Day | Aeration | [5 empty] | x | x
12 | Develop a Site Specific Model for Operator Training |  |  | Hourly | Day or Week | Sludge Production |  |  | Typical control variables | Typical process indicators | x | x | x
|  |  |  | Minutes | Day | Aeration | [5 empty] | x | x
INDUSTRIAL
13 | Develop a Process Configuration for Nitrogen Removal Treating Waste from a Food Production Factory (Soy Sauce) |  |  | Minutes | Week | Nitrogen removal |  |  | Conf, aerator timings | NH3 NO3 NO2 DO | x | x | x
14 | Assess Acceptability of New Influent at a Petrochemical Site | Monthly Seasonal | Capacity | [5 empty] | Q | COD,QWAS, Qair, DO | x |  | x

## Ch 6 table 2
Inputs & Outputs
Suggested Format
# | Objectives | Parameters/Manipulated Variables | Main Outputs | Summary Table | Time Series Graph | Bar Chart | Cumulative Distribution
DESIGN
1 | Calculate Sludge Production | QWAS | FWAS kg d | x
x
2 | Design Aeration System |  | Qair, % coverage, airflow per diffuser | x | x |  | x
[5 empty] | x |  | x
[5 empty] | x |  | x
3 | Develop a Process Configuration for Nitrogen Removal | V, Qrec, conf | Ntot | x |  | x
4 | Develop a Process Configuration for Phosphorus Removal | V, Qrec, conf | Ntot, Ptot | x |  | x
5 | Assess Plant Capacity for Nitrogen Removal | Q, qAir | Ntot | x |  | x
6 | Design a Treatment System to Meet Peak Effluent Nitrogen Limits | Qair, V, config | NHx, Nox |  | x |  | x
OPERATION
7 | Optimise Aeration Control | Qair, DO set-points | kWh, Qair, NHx, NO3, NO2, DO |  | x | x
8 | Test Effect of Taking Tanks Out of Service | number of tanks | NHx, Ntot, Ptot |  | x
9 | Use Model to Develop Sludge Wastage Strategy | FWAS kg/d | MLSS |  | x
10 | Develop a Strategy to Handle Storm Flows | Q, Eq Basin V | NHx, Ntot, Ptot, TSS |  | x
TRAINING
11 | Develop a General Model for Process Understanding | Typical control variables | Typical process indicators | x | x | x
[5 empty] | x | x
12 | Develop a Site Specific Model for Operator Training | Typical control variables | Typical process indicators | x | x | x
[5 empty] | x | x
INDUSTRIAL
13 | Develop a Process Configuration for Nitrogen Removal Treating Waste from a Food Production Factory (Soy Sauce) | Conf, aerator timings | NHx, NO3, NO2, DO | x | x | x
14 | Assess Acceptability of New Influent at a Petrochemical Site | Q | COD,QWAS, Qair, DO | x |  | x