## Read Me
Disclaimer
This design template is developed by the Bohol Environment Management Office (BEMO) in cooperation with the Philippine Environmental Governance 2 (EcoGov2) Project which may be used and reproduced. This design template is based on Reed's Method for constructed wetland design. The programmer does not claim liability on any error, loss or damage that may arise from using this design template. The user is required to test and verify the results. The organization or person using this template shall bear the risk and responsibility of controlling the quality and performance of the constructed wetland.
For any comment and suggestion, please contact:
Bohol Environment Management Office
email: bemobohol@yahoo.com
How To Use This Template:
REED'S METHOD PAGE 1 - Encode all the data in the required fields. Required fields are bold and red in color. These data are flow rate, influent BOD, target BOD, retention time, wetland depth, void volume, hydraulic conductivity of the medium and slope of wetland bed. Additional information in the required fields are the reference temperature, water temperature, rate constant at reference temperature and temperature coefficient for rate constant. The values can be found in RATE CONSTANT sheet. The computed wetland dimension is bold and blue in color.
REED'S METHOD PAGE 2 - Encode all the data in the required fields. Required fields are bold and red in color. This data are the influent concentrations of pathogens, total suspended solids and total phosphorous. Additional information needed for the computation of pathogen removal are the rate constant at reference temperature, temperature coefficient and the number of cells of the wetland. Computed effluent wastewater quality based on the designed size is bold and blue in color.

## Rate Constant
Temperature coefficient for rate constant for Reed et al, (1995a) Design Equations
Parameter | BOD | Nitrificationb | Denitrificationb | Pathogen
| Removal | NH4 Removal | NO3 Removal | Removal
TR (0C) | 20 | 20 | 20 | 20
Residual (mg/l) | 6 | 0.2 | 0.2
FOR FREE WATER SURFACE WETLANDS (FWS):
KR (day-1) | 0.678 | 0.2187 | 1 | 2.6
θR | 1.06 | 1.048 | 1.15 | 1.15
FOR SUB-SURFACE FLOW WETLANDS (SSF):
KR (day-1) | 1.104 | KNHc | 1 | 2.6
θR | 1.06 | 1.048 | 1.15 | 1.19
a All rate coefficient are for temperature greater than 10C
b nitrification/denitrification are not possible at temperatures below 00C
c KNH = 0.01854 + 0.3922(rz)2.6077
where: | KNH is SSF nitrification rate constant (day-1)
rz is depth of bed occupied by root zone (percent, expressed as decimal fraction)
developed by Bohol Environment Management Office
in cooperation with The Philippine Environmental Governance 2 Project

## Porosity n
Porosity n for unconsolidated sedimentary materials from Morris and Johnson, 1967
MATERIALS | POROSITY n
%
Gravel, Coarse | 24 to 37
Gravel, Medium | 24 to 44
Gravel, Fine | 25 to 39
Sand, Coarse | 31 to 46
Sand, Medium | 29 to 49
Sand, Fine | 26 to 53
Silt | 34 to 61
Clay | 34 to 57
developed by Bohol Environment Management Office
in cooperation with The Philippine Environmental Governance 2 Project

## Hydraulic Conductivity Ks
Hydraulic Conductivity Ks for unconsolidated sedimentary materials from Domenico and Schwartz, 1990
MATERIALS | HYDRAULIC CONDUCTIVITY Ks
m3/m2.day
Gravel | 25.92 to 2592.00
Sand, Coarse | 0.07776 to 518.40
Sand, Medium | 0.07776 to 43.20
Sand, Fine | 0.01728 to 17.28
Silt | 0.0000864 to 1.728
Clay | 0.000000864 to 0.00040608
developed by Bohol Environment Management Office
in cooperation with The Philippine Environmental Governance 2 Project

## Reed's Method
Constructed Wetland Design Template
Reed's Method
Page 1
Data:
| Flow rate (Q) | : | 14 | m3/day | Wetland Depth (y) | : | 0.6 | m
| Influent BOD (Ci) | : | 150 | mg/L | Porosity (n) | : | 0.35 | %
| Target BOD (Ce) | : | 50 | mg/L | Hydraulic Conductivity (kS) | : | 500 | m3/m2.day
| Retention Time (t) | : | 1.5 | days | Slope (S) | : | 0.015 | m/m
Values From Temperature Coefficient for Rate Constant for Reed Design Equations
| Water Temperature (Tw) | : | 25 | 0C | Rate Constant at Reference Temperature (KR) | : | 1.104 | day-1 | for BOD
| Reference Temperature (TR) | : | 20 | 0C | Temperature Coefficient (θR) | : | 1.06 |  | for BOD
Computation:
| Solve for porosity (n) |  |  |  | Typical Wetland Dimension | :
| n | : | VV/VT |  | length L | : | 23.9018 | m
|  | : | 0.35 |  | width W | : | 3.1111 | m
| Solve for Rate Constant (KT) |  |  |  | depth y | : | 0.6 | m
| KT | : | KRθR(TW-TR) |  | Actual Retention Time | :
|  | : | 1.4774 |  | t | : | Asyn/Q
| Solve for Wetland Treatment Area (As) |  |  |  |  | : | 1.1154 | days
| As | : | [Q(lnCi - ln Ce)]/(KTyn) |  | Hydraulic Loading Rate | :
| As | : | 74.3611 | m2 | HLR | : | 100Q/As
| Solve for Cross-sectional Area of Wetland Bed (Ac) |  |  |  |  | : | 18.827 | cm/day
| Ac | : | Q/ksS
|  | : | 1.8667 | m2
Solve for Wetland Bed Width (WB)
| WB | : | Ac/y
|  | : | 3.1111 | m
developed by Bohol Environment Management Office
in cooperation with The Philippine Environmental Governance 2 Project
Constructed Wetland Design Template
Reed's Method
Page 2
Computed Effluent Quality based on the design size of the Constructed Wetland:
Effluent BOD concentration
| Ce | : | Ci exp(-AsKTyn/Q)
|  | : | 28.8675 | mg/L
Total Suspended Solid Removal
For SSF Wetlands
| Ce | : | Ci(0.1058+0.0011HLR) |  | Influent Total Suspended Solid (Ci) | : | 0 | mg/L
|  | : | 0 | mg/L
For FWS Wetlands
| Ce | : | Ci(0.1139+0.00213HLR)
|  | : | 0 | mg/L
Pathogen Removal
| Ce | : | Ci/(1+tKT)N |  | Influent Pathogen (Ci) | : | 0 | per 100 mL
|  | : | 0 | per 100 mL | Rate Constant at Reference Temperature (KR) | : | 0
[5 empty] | Temperature Coefficient (θR) | : | 0
[5 empty] | Rate Constant (KT) | : | 0 | day-1
[5 empty] | Number of Cells (N) | : | 0
Total Phosphorous Removal
| Ce | : | Ci e(-Kp/HLR) |  | Influent Total Phosphorous concentration (Ci) | : | 0 | mg/L
|  | : | 0 | mg/L | phosphorous reaction rate (Kp) | : | 2.73 | cm/day
developed by Bohol Environment Management Office
in cooperation with The Philippine Environmental Governance 2 Project
Constructed Wetland Design Template
Reed's Method
Typical Top View
3.1111
23.9018
developed by Bohol Environment Management Office
in cooperation with The Philippine Environmental Governance 2 Project
Constructed Wetland Design Template
Reed's Method
Typical Cross Section
0.6
23.9018
Slope:
BED SLOPE for SSF wetland should be 2% or less while that for FWS should be 0.5% or less.
Freeboard:
Freeboard X is variable depending on the elevation of the piping system.
Typical Dimension:
Typical dimensions may not be followed as long as the treatment area of the wetland is maintained.
developed by Bohol Environment Management Office
in cooperation with The Philippine Environmental Governance 2 Project
0.75
0.50
0.15
0.15
0.50
0.75
0.15
EMERGENT MACROPHYTES
0.20
X
GRAVEL FILTER MEDIA
0.15